## Checklist
Commissioning Checklist
Specification and component compliance
- System drawing included |  | Yes |  | No
- Solar PV installed |  | Total capacity : ___________Wp (DC)
Brand : ___________
Model : ___________
Amount : ___________ panels
- Inverter installed |  | Total capacity : ___________Watt (AC)
Brand : ___________
Model : ___________
Amount : ___________ panels
- Panel tilt angle : |  | ________________ ºC
- Panel Orientation |  | ________________
- System BOQ / BOM ( Bill of Material ) included :
|  | Yes |  | No
- Mounting type :
|  | Tiled roof |  | Flat roof
|  | Sheet metal roof |  | Other : ________________
- Surge Protection Device installed :
|  | Yes |  | No
- Solar PV module S/N recorded :
|  | Yes |  | No
- Inverter S/N recorded :
|  | Yes |  | No
Performance Verification (take these values at the same time)
MEASURE and OBSERVE
- Module Temperature (Tcell) : | ________________ °C |  | * Use an IR thermometer of PV module temperature sensor
- Ambient Temperatire (Tamb) : | ________________ °C |  | * A general guideline to estimate module temperature:
800-1000W/m2 = 25°C above ambient
400-799W/m2 = 15°C above ambient
200-399W/m2 = 5°C above ambient
- Irradiation Corrected Value (Irc) : | ________________ Watts/m2 |  | * Use a pyranometer (handheld or already installed)
- Power production (Pinv) : | ________________ Watts |  | * Observed power production at the grid inverter
- Inverter AC output : | ________________ VAC
- Inverter frequency : | ________________ Hz
CALCULATE
- Temperature Correction (Tcorr) : | ________________ |  | * Tcorr = 1 + Module Temp Corr. Factor * (Tcell-25)
- Irradiance Correction (IRcorr) : | ________________ |  | * IRcorr = 1000 / IRc
- Shading losses (SF): | ________________ % |  | * There should be no shading at any time of the day
- Inverter Efficiency (InvEff): | ________________ |  | * Check the inverter's efficiency curve at current power
- Adjusted Power (Padj) : | ________________ Watts |  | * Padj = STC power * Tcorr * IRcorr * SF * InvEff
- Power Variation (Pvar) : | ________________ % |  | * Pvar should be <10%; excellent systems are typically <5%
ADDITIONAL MEASUREMENTS
- Each string cvoltage (Voc) on sunny day ( inverter off ) check at DC disconnect or string combiner box :
string 1 : __________________________ VDC
string 2 : __________________________ VDC
string 3 : __________________________ VDC
- Each string current (Isc) on sunny day ( inverter off ) check at DC disconnect or string combiner box :
string 1 : __________________________ Amp
string 2 : __________________________ Amp
string 3 : __________________________ Amp
Installation Inspection
|  |  |  | YES | NO | N/A
- PV module and module wiring
- Module cables secured properly
- Module connectors are properly connected
- Bending radius < 4 times wire diameter
- No debris on module surface
- No physical damage on module
- String layout clearly marked
- All hardware installed as designed
- All fasteners are properly rorqued
- All buillding penetration points are weather sealed properly
- DC conduit labeled with "WARNING : HIGH DC VOLTAGE"
- All DC junction boxes are securely fastened and sealed against weather
- Dfrip loops incorporated into all appropriate entry points
- All components are clearly and accurately marked on layout drawings
- Wiring in all combiner boxes are routed neatly
- All wire identified with permanent labels
- Warning label on all DC fuses, disconnect and circuit breakers with : " Do not remove or disconnect under load. DC voltage present"
- Inverter physically installed and located per manufacture's ventilation and installation specification
- Verify inverter time and date are set correctly ( if applicabble )
- Monitoring system working properly ( if applicable )
- All manuals and documentation are located in the same location
- All cables exposed to the environment are UV resistant and reted to wet service or installed in UV resistant conduit
- All PV cabling are flexible / multi strand
- Cables and other PV components and its monitoring system do not obstruct water drain paths
- All cables afre protected from abration, tension, compression, and cutting force
- Verify polarity of all connections
- PV array max. voltage < 600VDC for residential installations
- No shading on module during daylight hours
- All wiring is neat and secure
- All wiring is not easily accessible
- Dissimilar metals are electrically isolated to prevent galvanic corrosion
- Aluminium components are not placed indirect contact with concrete
- All installation methods must be neat and permanent
System Documentation and Owner Education
- Manufactures instructions for :
|  | PV module |  | Inverter
Surge Protection Devide
- Site drawings :
|  | Yes |  | No
- Electrical diagrams :
|  | Single line |  | Bill of materials |  |  | `
3 - line
- Array Mounting Drawing :
|  | Yes |  | No
- Owner training session :
Basic system operation
Turn on and shutdown procedure
Reading on-board display
Reading monitoring system if not on-board
Required routine maintenance and inspection
Emergency contact
`