## WMC
Workmanship Checklist
General Checklist
1 | No visible damage to any equipment
2 | Safe access to all necessary equipment for inspection and maintenance
3 | All circuit breakers, fuses, switches and disconnects clearly labeled with their ratings
4 | Schematic diagram of the system is posted clearly on a durable material
5 | Each component clearly labeled (fuses, breakers, switches, wires)
6 | Cable color code complies with local regulations
7 | All metal parts protected adequately against corrosion
8 | All joints at metal conduit are mechanically sound and electrically continuous
9 | Metal conduits are adequately earthed
10 | All exposed metal parts and enclosures are adequately earthed with approved mechanical bonding
11 | Overhead lines are high enough to avoid traffic damage (minimum 4 meters for human traffic only)
12 | Cables adequately protected against mechanical damage (including abrasion on rough surfaces)
13 | DC cabling separated between positive and negative
14 | Grounding system installed according to regulations
15 | Surge protection devices installed properly
16 | DC disconnects and AC disconnects installed properly, labeled clearly and easily accessible
17 | All installed equipment comply to the engineering drawings and documentations
18 | All cables and protection devices have been calculated to withstand the electrical current
19 | All cables are protected from damage
20 | Warning notices and labels installed properly and made of durable materials
21 | All bolts and screws are torqued to specification (including on breakers and fuse holders)
22 | All mechanical mounting devices are secure and level
23 | Solar PV mounting system was installed to manufactuer's specification and safety codes
Example Detailed Checklist (according to local safety and building codes)
1 | Grounding electrode resistance measurement of less than 25 ohms (as tested per regulation)
2 | Overhead wires installed at more than 5.2 meters (foot traffic) or 5.8 meters (vehicle traffic)
3 | Solar PV panels are not shaded at any time of the day and in the foreseeable future
4 | Rooftop mounting system did not damage the roof integrity
5 | Unprotected outdoor cables are UV resistant and rated for outdoor use without protection
6 | Solar PV panels are at least 100mm from the roof surface
7 | MCB terminal screws are tightened to 1.7Nm (or as specified by the manufacturer)

## Sheet2
PT. Anekatek Consultants
Gajah Mada Tower Lt 22 N0 19 -26, Petojo, Jakarta Pusat
Operational Office : TRIO Building, Jl. Mampang No 16 – 17 Jakarta Selatan
Tel:+ 62 21-99490770 +62 (0)21-3901007/email:info@aeconsults.com
PT. Anekatek Consultants
Gajah Mada Tower Lt 22 N0 19 -26, Petojo, Jakarta Pusat
Operational Office : TRIO Building, Jl. Mampang No 16 – 17 Jakarta Selatan
Tel: + 62 21-99490770 +62 (0)21-3901007 / email: info@aeconsults.com